# 5310PC	POTTER SUSPENDED CEILING PANELS AND GRID

## 1.	GENERAL

This section relates to the manufacture, supply and installation of Potter Interior Systems Ltd and USG suspended ceiling systems, including all elements offered by the manufacturer to complete the system.

### 1.1	DOCUMENTS

Documents referred to in this section are:

AS/NZS 1170.1	Structural design actions - Permanent, imposed and other actions

NZS 1170.5	Structural design actions - Earthquake actions - New Zealand

AS 1530.3	Methods for fire test on building materials, components and structures

- Simultaneous determination of ignitability, flame propagation, heat release and smoke release

AS 1530.4	Methods for fire tests on building materials, components and structures - Fire-resistance test of elements of construction

AS/NZS 2589	Gypsum linings - Application and finishing

AS/NZS 2785	Suspended ceilings - Design and installation

AS/NZS 3837	Method of test for heat and smoke release rates for materials and products using an oxygen consumption calorimeter (cone test)

NZS 4219	Specification for seismic resistance of engineering systems in buildings

ASTM C423	Test method for sound absorption and sound absorption coefficients by the reverberation room method

ASTM C635	Standard specification for the manufacture, performance and testing of metal suspension systems for acoustical tile and lay-in panel ceilings

ASTM E1414	Standard test method for airborne sound attenuation between rooms sharing a common ceiling plenum (two room method)

Documents listed above and cited in the clauses that follow are part of this specification.  However, this specification takes precedence in the event of it being at variance with the cited document.

### 1.2	MANUFACTURER’S DOCUMENTS

Manufacturer’s and supplier’s documents relating to work in this section are:

USG Lifetime Warranty

USG Clean Room ClimaPlus

USG Eclipse ClimaPlus

USG Frost ClimaPlus

USG Impressions ClimaPlus

USG Mars ClimaPlus

USG Olympia Micro ClimaPlus

USG Premier Hi-Lite ClimaPlus

USG Radar ClimaPlus

USG Radar ClimaPlus High CAC/High NRC

USG Radar Illusion ClimaPlus

USG Rock Face ClimaPlus

USG Donn® Brand Grid Suspension Systems

USG Fire Rated Exposed Grid Ceiling System

USG Early Fire Reaction - AS/NZS 3837

USG Seismic Design Guide

USG Donn® ScrewFix™ Plasterboard Suspension System

USG ScrewFix™ Ceiling Batten System

USG Drywall Grid Suspension System

USG Maintenance Guidelines

USG Geometrix™ Metal Pan

Copies of the above literature are available from Potter Interior Systems Ltd

Web:	www.potters.co.nz

Email:	info@potters.co.nz

Telephone:	0800 POTTER (0800 768 837)

Facsimile:	09 579 5661

### 1.3	ABBREVIATIONS

The following abbreviations are used throughout this part of the specification:

NRC	Noise reduction coefficient

CAC	Ceiling attenuation class

STC	Sound transmission class

AWCINZ	Association of Wall and Ceiling Industries of New Zealand Inc

### 1.4	NO SUBSTITUTIONS

Substitutions are not permitted to any specified system, or associated components and products.

### 1.5	INSTALLATION

To AS/NZS 2785.  Installation by a manufacturer’s accredited installer, using the manufacturer’s technical services.  Accredited installers must be members of the AWCI.  Provide evidence of experience, listing completed projects of similar size and complexity.

Installation to comply with the loadings code AS/NZS 1170 and NZS 1170.5.  Installation to comply with the requirements of NZS 4219; with related building services installations complying specifically with clauses 2.22, 2.25 and 2.29.

### 1.6	SUPPLY WARRANTY

Supply a warranty as follows:

Type:	USG’s System Lifetime Warranty

(maximum 30 years - exposed grid and acoustical panel)

Donn® suspension system (15 years)

USG acoustical ceiling panels (15 years)

USG Drywall Grid suspension system (15 years)

USG Donn ScrewFix suspension system (15 years)

## 2.	PRODUCTS

Materials - exposed grid system

### 2.1	SUSPENSION SYSTEM

Brand:	USG Donn®

Grid finish/colour:	Pacific White

Materials:	Hot-dip galvanized steel

Compliance:	AS/NZS 2785, AS/NZS 1170, NZS 1170.5, ASTM C635

AS 1530.4 for fire rated system

### 2.2	PERIMETER TRIM

Brand/form:	USG Donn®

Material:	Hot-dip galvanized steel

Finish/colour:	Pacific White

### 2.3	CEILING TILES

Brand:	USG

Edge profile:	To suit grid

Performance:	ASTM C423, ASTM E1414

AS 1530.4 for fire rated system

Materials - suspended flush ceilings

### 2.4	SUSPENSION SYSTEM

System:	USG Drywall Grid suspension system or USG Donn®

ScrewFix™ plasterboard suspension system

Finish:	Hot-dip galvanized steel

Compliance:	AS/NZS 2785, AS/NZS 1170, NZS 1170.5, ASTM C635

AS 1530.4 for fire rated system

### 2.5	PLASTERBOARD SHEET

Gypsum plaster core encased in a durable face and backing papers.

### 2.6	FIBROUS PLASTER SHEET

Gypsum plaster, casting grade reinforced with fibreglass.

Components

### 2.7	SCREWS

Screws to suit the lining manufacturer.

## 3.	EXECUTION

### 3.1	CO-ORDINATE SERVICES

Co-ordinate and co-operate with electrical and mechanical work to avoid conflict between suspension members and luminaires, diffusers, pipework and ducting.  Confirm the provision of extra hangers and fixings.

Ensure co-operation with work in and above the ceiling, including the marking of specific ceiling tiles below major access points to above-ceiling services.  Colour coded markings to follow the standards laid down by mechanical and electrical services.

### 3.2	SITE CONDITIONS

Do not begin installation until the building is closed in, fully glazed, the roof watertight, and mechanical and electrical duct work above the ceiling completed.

### 3.3	INSTALL

Install the system to AS/NZS 2785 minimum standards and the ceiling manufacturer's requirements.

### 3.4	ACCESSIBILITY

Provide access to the ceiling system and the in-ceiling and above-ceiling services so that maintenance and removal of all parts can be carried out without damage to the ceiling system or panels.

### 3.5	PENETRATIONS

Accommodate recessed light fittings, air conditioning outlets and other electrical and/or mechanical services that are fixed to or pass through the ceiling system.  Provide independent support for these as necessary; ceiling tiles must not support their weight.

### 3.6	FLUSH CEILING

Install the suspension system to AS/NZS 2785 minimum standards.  Screw-fix sheets to sections at the centres required by the ceiling lining manufacturer to AS/NZS 2589.  Stagger joints and fully support on sections, at centres to suit the load and the ceiling system manufacturer's requirements.  Refer to PLASTERBOARD LININGS for fibrous plaster or plasterboard stopping.

### 3.7	PROTECT EXISTING WORK

Protect adjacent existing work from damage during the installation.

### 3.8	REPLACE AND CLEAN

Replace all damaged or marked elements.  Clean all soiled or marked units.

### 3.9	REMOVE

Remove all debris, unused elements and elements from the site.

## 4.	SELECTIONS

### 4.1	SCHEDULE

Area:	~

Reference:	~

Fire rating:	~

Acoustical rating:	NRC: ~

CAC: ~

STC: ~

Materials - exposed grid system

### 4.2	SUSPENSION SYSTEM, ACOUSTICAL

Type:	Donn® ~

Module:	~ mm x ~ mm

Rail face:	~ mm

### 4.3	SUSPENSION SYSTEM, FIRE RATED

Type:	Donn® DXL Fire rated 24 mm face

Module:	~ mm x ~ mm

### 4.4	PERIMETER TRIM

Type:	~

### 4.5	CEILING TILES

Type/pattern:	~

Thickness:	~ mm

Size:	~ mm x ~ mm

### 4.6	CEILING TILES, FIRE RATED

Type/pattern:	~

Thickness:	~ mm

Size:	~ mm x ~ mm

Materials - suspended flush ceilings

### 4.7	SUSPENSION SYSTEM

Ceiling lining:	~

### 4.8	CEILING LINING

Brand:	~

Thickness:	~ mm

Type:	~

### 4.9	ACCESS HATCHES

Brand/type:	~

Location:	~

Edge detail:	~

Finish/colour:	~

Size:	~ mm x ~